TOWN OF BANCROFT WWTP

REPORT OF THE COMPREHENSIVE TECHNICAL ASSISTANCE

PHASE OF THE CCP AND CASE STUDY

# Report prepared by

# global facilitation Incorporated

# MAY 20TH  2020

“© 2020, The Corporation of the Town of Bancroft. All Rights Reserved. The preparation of this operational study was carried out with assistance from the Government of Canada and the Federation of Canadian Municipalities.  Notwithstanding this support, the views expressed are the personal views of the authors, and the Federation of Canadian Municipalities and the Government of Canada accept no responsibility for them.”

Table of Contents

1	Introduction	1

1.1	Background	1

1.2	application of the ccp in the U.S	1

1.3	application of the ccp in ontario	1

1.4	application of the ccp at the town of Bancroft WWTP	2

2	program methodology	3

2.1	composite correction program	3

2.2	total sludge mass control concept	3

3	bancroft wwtp	5

3.1	facility description	5

3.2	Liquid Train	5

3.3	Solids Train	7

4	2018 raw wastewater flow rate and characteristics	8

4.1	Flow rate	8

4.2	raw wastewater bod concentration	8

4.3	raw wastewater tss concentation	9

4.4	Raw wastewater tp concentration	10

4.5	raw wastewater tkn concentration	10

5	2019 raw wastewater flow rate and characteristics	12

5.1	flow rate	12

5.2	raw wastewater bod concentration	12

5.3	raw wastewater tss concentration	13

5.4	Raw Wastewater Tp Concentration	14

5.5	Raw waterwater tkn concentration	14

6	liquid train 1 2018 - process control	16

6.1	total sludge mass control	16

6.2	secondary clarifier solids residence time	17

6.3	liquid train svi	18

6.4	Activated sludge distribution	19

6.5	Return activated sludge flow rate study	20

7	liquid train 2 2018 - process control	23

7.1	total sludge mass control	23

7.2	Secondary Clarifier Solids Residence Time	24

7.3	liquid Train 2 svi	25

7.4	activated sludge distribution	26

8	liquid train 1 2019 - process control	27

8.1	total sludge mass control	27

8.2	secondary clarifier solids residence time	29

8.3	liquid train 1 svi	30

8.4	activated sludge distribution	30

9	liquid train 2 2019 - process control	32

9.1	total sludge mass control	32

9.2	secondary clarifier solids residence time	33

9.3	liquid train 2 svi	34

9.4	activated sludge distribution	35

9.5	return activated sludge flow rate	36

10	january 2018 to august 2019 – final effluent quality	37

10.1	bod5 concentration	37

10.2	tss concentration	38

10.3	total phosphorus concentraton	39

10.4	total ammonia nitrogen concentration	40

11	SLUDGE ACCOUNTABILITY ANALYSIS	42

11.1	function	42

11.2	typical industry sludge production values	42

11.3	actual sludge production at bancroft wwtp	42

11.4	results of sludge accountability analysis	42

11.5	interpretation of results	43

12	STEP FEED – storm flow management tool	44

12.1	application	44

12.2	Impact of not implementing step feed – case study	44

13	capacity demonstration	46

13.1	Waste Activated Sludge Thickening Study	46

13.2	results of the capacity demonstration	47

14	conclusions	48

14.1	viability of existing major unit processes	48

14.2	Total sludge mass control program	48

14.3	raw wastewater characteristics	48

14.4	stable process control	48

14.5	sludge accountability	48

14.6	step feed	49

15	RECOMMENDATIONS	50

15.1	Maintaining the existing physical infrastructure and equipment	50

15.2	viability of existing major unit processes	50

15.3	institutionalization of THE OPTIMIZATION PROGRAM	50

15.4	raw wastewater characteristics	50

15.5	stable process control	51

15.6	Step feed	51

15.7	operational strategy	51

# Introduction

## Background

In November 2017 the Canadian Federation of Municipalities approved the Application of the Composite Correction Program (CCP) to improve climate change resiliency of the Town of Bancroft’s wastewater system. Operating records have shown that the treatment is negatively impacted by high wastewater flows during rain or snow melt events. Compounding the challenge the Ontario climate change data portal predicts that through 2045, historic five year return period storms will be equivalent to historic two year return period storms. Also, the annual volume of precipitation will increase from 720 mm to 781 mm.  The CCP is equipped with tools that enable the operations staff to “operate around” current and future high flow events, without significantly impairing the quality of the treated wastewater.

## application of the ccp in the U.S

The CCP was originally developed by the United States Environment Protection Agency (EPA). In 1972 the U.S. Federal Government launched the Construction Grants Program. The program provided $30 billion for the construction of wastewater treatment plants. However in 1980, surveys showed that 60% of treatment plants did not comply with their discharge permits, more than half of the time. In response to this significant rate of non-compliance, the Office of Research and Development of the U.S. EPA initiated studies that led to the development of the CCP. After applying the program at wastewater treatment plants in the U.S. the facilities were optimized and achieved their compliance permits. In many instances major capital expenditure was either delayed or postponed. The primary lesson learned was, while the newly constructed treatment plants were adequately designed, it was evident that other non-design performance limiting factors were preventing many new treatment plants from achieving their discharge permits.

## application of the ccp in ontario

In Ontario prior to 1990, under Policy 08-01 the “Guidelines for the Determination of Treatment Requirements for Municipal and Private Sewage Treatment Works Discharging to Surface Waters”, secondary treatment plants were required to achieve annual average treated effluent BOD5 and TSS concentrations of 25 mg/L. More stringent limits could be imposed based on local receiving water quality protection needs. In 1990, the Ministry of the Environment, Conservation and Parks in consultation with industry, municipal, and public representatives agreed that the Municipal Industry Strategy for Abatement (MISA) would set treated effluent limits based on monthly averages in addition to annual averages.

In 1991, the Ministry of the Environment, Conversation and Parks, in partnership with Environment Canada implemented a study with the following objectives:

- To identify factors that contribute to poor performance at Ontario municipal sewage treatment plants.

- To identify, evaluate, and demonstrate procedures for improving the ability of existing sewage treatment plants to meet current and future Ontario compliance limits, while minimizing major construction costs.

Between 1992 and 1994 the U.S. EPA CCP was applied at three wastewater treatment plants in Ontario. The objectives of applying the CCP were:

- To understand the suitability of the U.S. EPAs CCP for application in Ontario.

- To understand the qualifications and skills required to implement the CCP techniques.

- To understand the level of training required to enable staff to competently complete the CCP.

- To recommend what changes or modifications, if any, that would be required prior to widespread application of the CCP in Ontario.

In 1995, following the completion of applying the CCP at the three wastewater treatment plants in Ontario, the study concluded that the program was a valuable tool for resolving performance limiting factors at existing treatment plants. No major modifications to the approach were required prior to broad-scale application in Ontario.

## application of the ccp at the town of Bancroft WWTP

In 2009, the existing liquid train at Bancroft WWTP was twinned at a capital cost of $9 million. The capital investment placed financial pressure on the Town of Bancroft, resulting in a 100% increase in wastewater rates to residents and businesses in 2017. The approach to applying the CCP at Bancroft was to look for opportunities to re-rate the facility. If the re-rating is successful in 2020, the Town will be in a position to delay when the next major capital investment is required.

# program methodology

## composite correction program

The first step of the CCP is a Comprehensive Performance Evaluation (CPE), which is a detailed review of the facility to identify factors that limit treatment plant performance. The second step, Comprehensive Technical Assistance (CTA), is implemented by a skilled facilitator to systematically address the factors identified in the CPE, by transferring skills to treatment plant staff and management. Several published case studies in Ontario have shown that applying the CCP can lead to long-term improvements in both treatment plant capacity and performance while avoiding costly upgrades or expansion.

## total sludge mass control concept

Managing suspended growth systems requires utility staff to implement and maintain a stable level of process control.  Stable process control is especially important where utility staff choose to, or are required to achieve a higher level of treatment, such as nitrification. The aeration basin is the dynamo where treatment is achieved and sustained. To achieve stable nitrification, the activated sludge barrier must be scientifically managed. An adequate quantity of activated sludge is required in the aeration basin at all times to achieve the desired level of nitrification. Establishing process control conditions in the secondary unit processes that results in stable nitrification is a complex balance between carrying an adequate quantity of activated sludge to achieve the desired level of nitrification, while at the same time minimizing the mass of activated sludge in the secondary clarifier. The approach is called the Total Sludge Mass Control Concept. The concept has been adopted by the American Water Works Association (AWWA) as a way for utilities to demonstrate maximizing the effectiveness of the activated sludge barrier, similar to drinking water utilities using turbidity as a surrogate for minimizing the passage of pathogens through treatment barriers.

Schematic 1 is a visual illustration of the total sludge mass control concept. Implementing the total sludge mass control concept represents a more scientific approach to managing the activated sludge barrier. The approach involves measuring the mass of activated sludge in the aeration tank, and the secondary clarifier at the same time. The sum of the aeration tank mass and the secondary clarifier equals the total mass of activated sludge in the secondary unit processes. Using the sludge retention time (SRT) equation included in Schematic 1 the mass of activated sludge to waste is calculated on a daily basis. Repeating these measurements and calculating the mass of activated sludge to waste every day, enables the operating staff to achieve a higher and more stable level of process control. The same approach to managing the activated sludge barrier was implemented at Bancroft WWTP.

Schematic 1. Total Sludge Mass Control Concept

# bancroft wwtp

## facility description

The WWTP is owned by the Town of Bancroft and is operated by Veolia Water. The facility services a population currently estimated at 2,200.  The raw sewage is primarily residential in nature. The plant, an extended aeration process, is comprised of two parallel trains and has a nominal design flow of 1,632 m3/d.

## Liquid Train

The liquid train is equipped with inclined mechanical auger screens and vortex type grit removal equipment. The screened and de-gritted wastewater is discharged to two extended aeration plants. Each liquid train is comprised of an anoxic tank, an aeration tank and secondary clarifier. The aeration basins are equipped with fine bubble membrane diffusers. Air is diffused into the MLSS using two 50 HP positive displacement blowers.  Mixed liquor from the two aeration basins flows to two secondary clarifiers.  The clarifiers are circular and equipped with scum removal and continuous Return Activated Sludge (RAS) scraper blades that collect the settled solids on the floor of the clarifiers. The settled solids are returned to the anoxic and aeration tanks using RAS pumps.

Dissolved phosphorus in the raw wastewater is precipitated from solution by applying an Alum coagulant. The chemical coagulant converts the dissolved phosphorus to an insoluble precipitate that settles in the secondary clarifiers. The chemical precipitate is collected by the RAS pumps together with the MLSS and returned to the anoxic tanks.  Schematic 2 provides a flow diagram of the liquid and solids handling at the facility.

Schematic 2: Flow Diagram for Town of Bancroft WWTP

Following treatment in the aeration tanks and secondary clarifiers, the treated wastewater is pumped to two Ashbrook-Simon-Hartley tertiary filters. The function of the tertiary filters is to further reduce the suspended solids concentration before the treated wastewater is discharged to the York River. Typically, secondary effluent suspended solids range from 10 - 15 mg/L. Following tertiary filtration, typical suspended solids are less than 5 mg/L.

Following the tertiary filters, the treated wastewater is disinfected using ultraviolet light before being discharged to the York River. The disinfection equipment is comprised of two banks of low pressure, low intensity UV lamps.

## Solids Train

Waste activated sludge is pumped to an aerobic digester. The digester is equipped with a jet mixing system to circulate the contents of the aerobic digester. Following stabilization, the biosolids are hauled off-site and applied on agricultural land during the land application season.

# 2018 raw wastewater flow rate and characteristics

## Flow rate

Figure 1 includes the monthly average and daily flow rates from January to December 2018. Also included is the current rated and proposed re-rated capacity of 2,000 m3/d. The maximum day flow rate was 3,889 m3/d and occurred on April 26th.

Figure 1. 2018 Monthly Average and Daily Flow Rates

Figures 2 to 5 feature the same time period as Figure 1.

## raw wastewater bod concentration

Figure 2 depicts the monthly average and individual day raw wastewater BOD5 concentration. April was the lowest monthly average concentration at 133 mg/L, while July was the highest at 300 mg/L. The highest individual BOD5 concentration was 546 mg/L measured on January 23rd.

Figure 2. 2018 Monthly Average and Individual Raw BOD5 Concentration

## raw wastewater tss concentation

Figure 3 depicts the monthly average and individual day raw wastewater TSS concentration. As with the BOD5 values April was the lowest monthly average concentration at 210 mg/L, while August was the highest value at 408 mg/L. The highest individual TSS concentration was 705 mg/L also measured on January 23rd.

Figure 3. 2018 Monthly Average and Individual Raw TSS Concentration

## Raw wastewater tp concentration

Figure 4 depicts the monthly average and individual day raw wastewater TP concentration. April was the lowest monthly average concentration at 2.5 mg/L, and January was the highest concentration at 5.4 mg/L. The highest individual TP concentration was 13.9 mg/L measured on January 23rd.

Figure 4. 2018 Monthly Average and Individual Raw TP Concentration

## raw wastewater tkn concentration

Figure 5 depicts the monthly average and individual day raw wastewater TKN concentration. April was the lowest monthly average concentration at 12.2 mg/L with January the highest value at 51.8 mg/L. The highest individual TKN concentration was 139 mg/L measured on January 23rd.

Figure 5. 2018 Monthly Average and Individual Raw TKN Concentration

# 2019 raw wastewater flow rate and characteristics

## flow rate

Figure 6 illustrates the monthly average and daily flow rates from January to August 2019. Also included is the current rated and proposed re-rated capacity of 2,000 m3/d. The maximum day flow rate was 5,148 m3/d and occurred on April 15th. The maximum day flow rate in 2018 was 3,889 m3/d. The maximum day flow rate in 2019 was 32% greater than 2018. During this period only one treatment train was in service.

Figure 6. 2019 Monthly Average and Daily Flow Rates

Figures 7 to 10 feature the same time period as Figure 6.

## raw wastewater bod concentration

Figure 7 depicts the monthly average and individual day raw wastewater BOD5 concentration. May was the lowest monthly average concentration at 114 mg/L, while February was the highest at 225 mg/L. The highest individual BOD5 concentration was 275 mg/L measured on February 12th 2019. Compared with 2018, the highest individual BOD5 concentration measured in 2019 was 50% lower than the highest value measured in 2018.

Figure 7. 2019 Monthly Average and Individual Raw BOD5 Concentration

## raw wastewater tss concentration

Figure 8 depicts the monthly average and individual day raw wastewater TSS concentration. May was the lowest monthly average concentration at 156 mg/L, with June the highest value at 324 mg/L. The highest individual TSS concentration was 507 mg/L measured on February 12th. Compared with 2018, the highest individual TSS concentration measured in 2019 was 28% lower than the highest value measured in 2018.

Figure 8. 2019 Monthly Average and Individual Raw TSS Concentration

## Raw Wastewater Tp Concentration

Figure 9 depicts the monthly average and individual day raw wastewater TP concentration. May was the lowest monthly average concentration at 2.2 mg/L, with February the highest value at 4.1 mg/L. The highest individual TP concentration was 8.3 mg/L measured on January 29th. Compared with 2018, the highest individual TP concentration measured in 2019 was 40% lower than the highest value measured in 2018.

Figure 9. 2019 Monthly Average and Individual Raw TP Concentration

## Raw waterwater tkn concentration

Figure 10 depicts the monthly average and individual day raw wastewater TKN concentration. April was the lowest monthly average concentration at 14.7 mg/L. August was the highest value at 33.3 mg/L. The highest individual TKN concentration was 44.3 mg/L measured on February 12th. Compared with 2018, the highest individual TKN concentration measured in 2019 was 94% lower than the highest value measured in 2018.

Figure 10. 2019 Monthly Average and Individual Raw TKN Concentration

# liquid train 1 2018 - process control

## total sludge mass control

Figure 11 is the first actual example of the total sludge mass control concept introduced in Part 2. The chart quantifies the mass of activated sludge in liquid train 1 from February to December 2018. Liquid train 1 is comprised of an anoxic tank, an aeration tank, and secondary clarifier. The black trace depicts the target mass of activated sludge.  The target was 4,000 kg from February to May 2018. The target sludge mass was temporarily increased to 5,150 kg on June 1st 2018, in preparation for implementing the capacity demonstration by placing liquid train 2 on standby. The target was returned to 4,000 kg on June 12th when the final effluent TAN results confirmed 4,000 kg was an adequate mass of activated sludge to maintain complete nitrification, with one liquid train in service. The target sludge mass was increased to 5,000 kg on November 15th. It was anticipated lower wastewater temperatures during the approaching winter would reduce the nitrification efficiency, and possibly increase the final effluent TAN concentration.

Figure 11. Quantity of Activated Sludge Mass In Liquid Train 1

At Bancroft WWTP, the target sludge mass was scientifically derived, and was calculated based on (1) the amount of biological sludge produced, combined with (2) the amount of chemical sludge produced. The blue trace is the actual total sludge mass, and averaged 4,200 kg for the period. There were periods when the actual sludge mass was higher (April 2nd mass = 5,133 kg) and lower than the target (October 23rd = 3,482 kg). Variations of this amount are normal and are expected due to the variability in both the biological and chemical sludge produced. What is important is the operations staff increased the activated sludge wasting in April to lower the sludge mass towards the target, and decreased the wasting in October to increase the sludge mass towards the target.  This is the essence of the total sludge mass concept, with the operations staff making “data based” decisions to remain close to the target sludge mass.

The WWTP is required to achieve stringent final effluent Total Ammonia Nitrogen limits. Therefore, when calculating the target sludge mass, the operations staff were conservative when selecting what Solids Residence Time (SRT) to operate at. An SRT greater than 24 days was chosen to ensure an adequate barrier of activated sludge was maintained at all times to achieve consistent nitrification. The red trace represents the mass of activated sludge in the aeration basin, and averaged 2,800 kg. Nitrifying bacteria nitrify only in the presence of oxygen, therefore maximizing the mass of activated sludge in the aeration basin is vital to support consistent nitrification. The green trace represents the quantity of sludge mass in the secondary clarifier, and averaged 700 kg. The orange trace represents the quantity of sludge mass in the anoxic tank, and averaged 650 kg.

By measuring the mass of activated sludge in each unit process, the operations staff have a clear visualization and understanding of the relative mass of activated sludge under aeration compared with the sludge mass in the secondary clarifier, and anoxic tank. More importantly, the operations staff are able to observe the trends over time, and make the correct process control adjustment if there is a significant change in the quantity of activated sludge in each unit process.

Figures 12 to 15 feature the same time frame as Figure 11.

## secondary clarifier solids residence time

Implementing the sludge mass control concept enables several new and important process control parameters to be measured each day. An example is the length of time the activated sludge is stored in the secondary clarifier, before the sludge is returned to the aeration basin. The information enables the operations staff to make the correct adjustment to the RAS pumps speed to lower the sludge mass in the secondary clarifier. Minimizing the solids residence time in the secondary clarifier ensures the majority of the activated sludge is stored in the aeration basin where nitrification occurs. Figure 12 features the secondary clarifier solids residence time in liquid train 1.

Figure 12. Liquid Train 1 Secondary Clarifier Solids Residence Time

Two distinct trends are observed in Figure 12. From February through May the solids residence time averaged 2 hours. From June to December the average solids residence time was 4 hours. Starting June 1st, liquid train 2 was place on standby and all of the raw wastewater was treated in liquid train 1. Doubling the load treated in liquid train 1 meant the production of biological and chemical sludge also doubled. This explains the increase in the solids residence time to 4 hours starting in June.

## liquid train svi

A parameter that measures the stability of activated sludge is Sludge Volume Index (SVI). Figure 13 features liquid train 1 SVI. Between February and March the SVI ranged from 100 up to 160. Starting in April, a new level of stability emerged with the SVI remaining at 100 for the remainder of the year. The minor degree of variability in the SVI is indicative of very stable process control, and confirms the operations staff accurately interpreted the data, and made the correct process control adjustments each day.

Figure 13. Liquid Train 1 SVI

## Activated sludge distribution

Another important parameter to monitor and manage is the distribution of activated sludge in the anoxic tank, aeration basin, and secondary clarifier. This is particularly important at WWTPs that are required to nitrify. Nitrification takes place in the aeration basin. Nitrifying bacteria only nitrify under aerobic conditions, therefore maximizing the mass of activated sludge under aeration is vital to ensure consistent nitrification. Figure 14 depicts the % distribution of activated sludge in liquid train 1. The orange trace represents the % of activated sludge in the anoxic tank.  The red trace represents the % of activated sludge in the aeration basin. The black trace represents the % of sludge mass in the secondary clarifier.

Figure 14. Distribution of Activated Sludge in Liquid Train 1.

The percentage of activated sludge in the anoxic tank ranged from 10% starting in February to 18% in December. The percentage of activated sludge under aeration ranged from 80% starting in February down to 64% in December. The percentage of activated sludge in the secondary clarifier ranged from 10% starting in February up to 20% in December. While the actual % distribution of activated sludge is unique to each WWTP, it is always desirable to make the correct process control adjustment that maximizes the mass of activated sludge in the aeration basin where treatment occurs.

## Return activated sludge flow rate study

A study was implemented in liquid train 1 that involved progressively lowering the RAS flow rate, and measuring  the distribution of the sludge mass in the aeration basin and secondary clarifier. Figure 15 illustrates the RAS % flow rate.

Figure 15. Liquid Train 1 % RAS Flow Rate

When the study was first started the % RAS flow rate ranged from 100% up to 140%. Starting in March, the operations staff started to incrementally reduce the RAS % flow rate until a flow rate of 40% was achieved in November. Lowering the RAS flow rate provided more time for the activated sludge to settle and thicken on the floor of the secondary clarifier, before being returned to the secondary treatment. Table 1 summarizes the results of the study. By reducing the RAS flow rate from 731 m3/d in March to 387 m3/d in December 2018 the operations staff achieved a significant increase in the RAS concentration from 6,176 mg/L up to 16,769 mg/L. This equates to an almost three fold increase in RAS concentration. By increasing the RAS concentration, the operating staff achieved a significant reduction in the WAS flow rate from 17 m3/d in July 2018 to 5 m3/d in March 2019. The reduction in the WAS flow rate increased the storage time in the aerobic digester, and reduced the need for decanting supernatant from the aerobic digester back to the liquid train. In March 2018, the average MLSS concentration was 4,172 mg/L, and 4,528 mg/L in December 2018. These are comparable values, and confirms the increase in the RAS concentration was achieved by reducing the RAS flow rate, and not by increasing the MLSS concentration. The RAS mass removed from the clarifier increased from 4,514 kg/d in March to 6,489 kg/d in December. This equates to a 44% increase the RAS mass transferred per day. Metcalf and Eddy design handbook for wastewater treatment calculates the theoretical Hydraulic Retention Time (HRT) in the aeration basin by dividing the volume of the aeration basin by the plant flow rate. However, the actual HRT includes the RAS flow rate in addition to the plant flow rate. Reducing the RAS flow rate by half achieved two important process control objectives, (1) the actual HRT in the aeration basin was increased, and (2) the oxidation pressure in the aeration system was maximized.

Table 1. Results of RAS Flow Rate Study

# liquid train 2 2018 - process control

## total sludge mass control

Figure 16 depicts the quantity of activated sludge mass in liquid train 2 for the period February to May 2018.

Figure 16. Quantity of Activated Sludge in Liquid Train 2

Similar to liquid train 1 the target sludge mass (black trace) in liquid train 2 was 4,000 kg to support consistent nitrification. The actual sludge mass (blue trace) averaged 3,900 kg compared with the target of 4,000 kg. As with liquid train 1 there were days when the sludge mass was higher (4,462 kg Feb 23rd) than the target, and days when the sludge mass was lower (3,238 kg Mar 2nd). On both occasions the operations staff made the correct process control adjustment by wasting either more or less activated sludge to maintain the sludge mass close to the target.

Figures 17 to 19 feature the same time frame as Figure 16.

## Secondary Clarifier Solids Residence Time

Figure 17 features the secondary clarifier solids residence time in liquid train 2. The solids residence time averaged 0.8 hours, compared with 2 to 4 hours in train 1 (Figure 12). Train 2 secondary clarifier is newer and is equipped with more efficient sludge removal technology than train 1. This explains the lower solids residence time in train 2 compared with train 1.

Figure 17. Liquid Train 2 Secondary Clarifier Solids Residence Time

## liquid Train 2 svi

Figure 18 depicts the trend in SVI for train 2. The chart follows a similar pattern as train 1 (Figure 13). The SVI was stable with only minor variability from 100 up to 150. Starting in late March, the SVI never varied from 100, and is indicative of a stable and high level of process control.

Figure 18. Liquid Train 2 SVI

## activated sludge distribution

Figure 19 depicts the % distribution of activated sludge in train 2. The yellow trace represents the % of activated sludge in the anoxic tank. The red trace represents the % of activated sludge in the aeration basin. The black trace represents the % of sludge in the secondary clarifier.

Figure 19. Distribution of Activated In Liquid Train 2

The percentage of activated sludge under aeration ranged from 62% to 80%.  The percentage of activated sludge in the secondary clarifier ranged from 4% to 10%, compared with 17% in train 1. For the anoxic tank the percentage of activated sludge ranged from 10% to 18%.

# liquid train 1 2019 - process control

## total sludge mass control

Figure 20 tracks the quantity of activated sludge in train 1 for the period January to  May 2019. The target sludge mass was adjusted several times in response to changing conditions. From January 1st to February 14th the target was 5,000 kg. The dark blue trace is the total sludge mass and is the sum of the (anoxic + aeration + clarifier ) sludge mass combined. The actual total sludge mass averaged 5,560 kg compared with the target of 5,000 kg. The red trace represents the mass of activated sludge in the aeration basin. The green trace represents the quantity of sludge mass in the secondary clarifier, and the yellow trace represents the quantity of sludge in the anoxic tank. From January to April 2019 the final effluent TAN concentration increased (see Figure 32) compared with the same period in 2018. The increase in 2019 is explained by one liquid train in service compared with two trains in 2018. To compensate, the operations staff increased the SRT.  A new target of 6,800 kg was adopted on February 15th and remained in place until March 6th. The final effluent TAN concentration remained high. In response, a new target sludge mass of 7,800 kg was adopted on March 6th and remained in place until May 4th when the final effluent TAN concentration returned to typical low values. Following the improvement in nitrification efficiency the operations staff selected a lower target of 4,000 kg that remained in place through August 2019.

Compounding the challenges with operating one liquid train, the wastewater flow rate increased significantly in April. The increase in flow rate started April 8th and peaked on April 15th at 5,148 m3/d. During this period of high flow rates, the activated sludge was transferred from the aeration basin to the secondary clarifier. The transfer is clearly evident in Figure 20 when the aeration sludge mass (red trace) was reduced from 4,700 kg on April 7th to 2,682 kg on April 9th. At the same time the clarifier sludge mass (green trace) increased from 1,723 kg on April 7th up to 4,000 kg on April 9th. From a nitrification perspective the transfer of activated from the aeration basin to the secondary clarifier was not ideal. Following the transfer, the majority of the nitrifying bacteria were in the secondary clarifier where conditions are not conducive to nitrification.

Figure 20. Quantity of Activated Sludge Mass in Liquid Train 1

## secondary clarifier solids residence time

Figures 21 to 23 include the same period as Figure 20. Figure 21 features the secondary clarifier solids residence time in liquid train 1. On June 1st liquid train 1 was removed from service for planned maintenance.

Figure 21. Liquid Train 1 Secondary Clarifier Solids Residence Time

There is a general downward trend in the data. The solids residence time ranged from four hours in January down to two in May. The downward trend is positive as it means the activated sludge was processed through the secondary clarifier in half the time in May compared with January.

## liquid train 1 svi

Figure 22 tracks the SVI in liquid train 1. The trend confirms the SVI is very stable and remained less than 100 for the entire five months. This is indicative of very stable process control with the operations staff making the correct process control adjustments each day.

Figure 22. Liquid Train 1 SVI

## activated sludge distribution

Figure 23 tracks the % distribution of activated sludge in the aeration basin, secondary clarifier, and anoxic tank. The red trace represents the mass of activated sludge in the aeration basin. The blue trace represents the quantity of sludge in the secondary clarifier, while the green trace represents the quantity of sludge in the anoxic tank.

Figure 23. Distribution of Activated Sludge in Liquid Train 1.

Between January and March the percentage of activated sludge under aeration (red trace) was stable at 65%. The distribution in the anoxic tank (green trace) was stable at 15%. For the secondary clarifier (blue trace) the distribution was stable at 20%. Starting in early April there was a significant shift in the distribution of activated sludge between the aeration basin and the secondary clarifier. The change in distribution coincided with the significant increase in plant flow rate starting April 5th. Between January and March the average day flow rate was 1,100 m3/d. For the month of April the average day flow rate was 3,348 m3/d, a three-fold increase compared with January to March. On April 15th the flow rate was 5,148 m3/d an approximate five-fold increase over the average of 1,100 m3/d. Starting April 5th, the higher flow rate caused the % distribution of activated sludge to be reduced from 65% to 45% in the aeration basin. The opposite occurred in the secondary clarifier, where the % distribution increased from 20% to 50%. The anoxic tank % distribution was reduced by a smaller amount from 15% to 10%. Starting in early May the flow rate returned to average values measured from January and March. The reduction in flow rate coincided with a return to the same % distribution of activated sludge that was present from January to April.

# liquid train 2 2019 - process control

## total sludge mass control

Liquid train 2 was returned to service on June 1st 2019 to enable planned maintenance in train 1 to proceed. Figure 24 tracks the quantity of activated sludge mass in liquid train 2 from May to August 2019.

Figure 24.  Quantity of Activated Sludge Mass in Liquid Train 2

Returning liquid train two to service entailed transferring all of the activated sludge from train 1 to train 2, using a mobile diesel pump. This explains the temporary increase in the total sludge mass (blue trace) from 4,800 kg on May 27th up to 8,574 kg on May 31st, and greater than the target of 5,900 kg. Following a period of planned wasting of surplus activated sludge, the total sludge mass was gradually reduced to 4,500 kg on July 10th. The target sludge mass was reduced to 4,000 kg on July 9th and remained at that value through August 2019.

## secondary clarifier solids residence time

The same timeframe used in Figure 24 is repeated in Figures 25 to 28. Figure 25 tracks the secondary clarifier solids residence time in liquid train 2. Starting in June the clarifier solids residence time reached 3.5 hours. In early July the solids residence time was reduced to less than 1 hour and remained at that low value through August.

Figure 25. Liquid Train 2 Secondary Clarifier Solids Residence Time

## liquid train 2 svi

Figure 26 depicts the SVI for liquid train 2. As with liquid train 1 the SVI in train 2 was very stable and never varied above 100. The excellent process control stability demonstrated in liquid train 2 in 2018 (Figure 18), was repeated in train 2 in 2019.

Figure 26. Liquid Train 2 SVI

## activated sludge distribution

Figure 27 depicts the % distribution of activated sludge in liquid train 2. The distribution of activated sludge ranged from 60% to 80% in the aeration basin, and a steady 20% in the anoxic tank. For the secondary clarifier the amount was 20% in June and reduced to less than 5% for the remainder of the period.

Figure 27. Distribution of Activated Sludge In Liquid Train 2

## return activated sludge flow rate

Figure 28 tracks the % RAS flow rate in liquid train 2. Prior to removing liquid train 1 from service in June 2019, the RAS % flow rate was 40%.  The operations staff elected to operate liquid train 2 at the same RAS % flow rate. This is an example of process control knowledge being transferred from one liquid train to another. The knowledge enabled the operations staff to confidently operate liquid train 2 at the same low RAS flow rate, that staff had previously demonstrated in liquid train 1 in 2018.

Figure 28. Liquid Train 2 % RAS Flow Rate

# january 2018 to august 2019 – final effluent quality

## bod5 concentration

Figure 29 depicts the monthly average final effluent cBOD5 results for the period January 2018 to August 2019. The red and light green traces represent the current ECA limit and objective, while the dark green and black traces represent the proposed ECA limit and objective. The concentrations for the proposed limit and objective are calculated based on a re-rated capacity of 2,000 m3/d. The monthly average final effluent cBOD5 results were all lower than both the current and proposed future limits and objectives. This highest individual sample measured for cBOD5 was 5 mg/L.

Figure 29. Final Effluent cBOD5 Concentration

## tss concentration

Figures 30 to 32 include the same time period as Figure 29. Figure 30 depicts the monthly average final effluent TSS results. The monthly average final effluent TSS results were all lower than both the current and proposed future limit and objective. The highest individual sample was 11 mg/L measured on April 15th 2019. In April 2019, the monthly average flow rate was 3,356 m3/d. The maximum day flow rate of 5,148 m3/d was also recorded on April 15th. With one train in service, a monthly average day flow rate of 3,356 m3/d is equivalent to four times the rated capacity of one train.

Figure 30. Final Effluent TSS Concentration

## total phosphorus concentraton

Figure 31 depicts the monthly average final effluent TP results. The switch to operating liquid train 1 only on June 1st 2018 required from July to September to stabilize and refine the control of alum coagulant for Total Phosphorus removal. During this period, the monthly average TP concentration ranged from 0.13 mg/L to 0.21 mg/L, compared with the proposed ECA limit of 0.16 mg/L. Once the operations staff fully understood how much alum was required to achieve the low proposed TP limit, the operations staff successfully managed the application of alum. Starting in October 2018 the monthly TP concentration was 0.09 mg/L, and remained less than the future proposed limit and objective. The highest individual sample result was 0.25 mg/L measured on September 4th 2018.

Figure 31. Final Effluent TP Concentration

## total ammonia nitrogen concentration

Figure 32 depicts the monthly average final effluent Total Ammonia Nitrogen (TAN) results. From January to May 2019 the monthly average TAN concentrations were higher compared with the same period in 2018. April 2019 was the highest monthly average TAN concentration at 3.6 mg/L, compared with the proposed ECA limit of 4.1 mg/L. The highest individual TAN sample result was 5.5 mg/L on May 5th 2019.

Figure 32. Final Effluent TAN Concentration.

Table 2 summarizes the operating conditions in April 2018 compared with April 2019. In April 2018 with two basins in service, the average HRT was 22 hours, the monthly average final effluent TAN concentration was low at 0.05 mg/L. In April 2019 and one basin in service, the average HRT was reduced to 6.4 hours, and significantly lower than April 2018. For context, the typical range of HRT in Metcalf and Eddy design handbook is 18 – 36 hours. The transfer of activated sludge from the aeration basin to the secondary clarifier, combined with the lower HRT in the aeration basin, puts in context the higher monthly average final effluent TAN concentration in April 2019.

At future projected flow rates and with both liquid trains in service, it is anticipated the proposed TAN ECA limit of 4.1 mg/L will not be exceeded.

Table 2. Operating Conditions in April 2018 Compared with April 2019

# SLUDGE ACCOUNTABILITY ANALYSIS

## function

Sludge accountability analysis is an important tool that enables utility staff to have confidence in the accuracy of the reported treated effluent data. The function of a sludge accountability analysis is to calculate the theoretical quantity of sludge that an activated sludge plant is expected to produce. The projected quantity of sludge is compared with the actual measured amount of sludge produced using process control data and plant records.

## typical industry sludge production values

Every wastewater treatment plant around the world that applies activated sludge to remove BOD, produces a typical mass of biological sludge. Similarly for TP removal metal coagulants are applied to precipitate the phosphorus out of solution, produce a typical mass of chemical sludge.  These industry sludge production values are used to calculate the projected sludge mass produced.

## actual sludge production at bancroft wwtp

The WAS flow rate per day multiplied by the solids concentration equals the actual mass of sludge produced at Bancroft. The WAS sample is a blend of biological and chemical sludge combined.

## results of sludge accountability analysis

Table 3 summarizes the results of the sludge accountability analysis for 2018. The table is comprised of 3 sections (1 the reported sludge mass, (2) the projected sludge mass, and (3) the formula for calculating the result.

Table 3. Results of the Sludge Accountability Analysis

## interpretation of results

A sludge accountability result of +/- 15 % is considered acceptable.

The sludge accountability analysis completed using records for 2018 closed within + 1.8 %. Over the one year period evaluated the difference between the projected sludge mass produced (71,196 kg)  and the reported sludge mass produced (69,910 kg) was only 1,286 kg. The difference is less than 4 kg of sludge per day that is not accounted for. Because the projected and reported sludge mass are so close, the flow rates and current sampling program are representative and there is a high level of confidence about the accuracy of the reported TSS loading to the York River.

# STEP FEED – storm flow management tool

## application

Step feed is a modification of the conventional activated sludge process. In conventional treatment mode wastewater enters at the beginning or head of the tank and flows through the entire tank. In step feed mode the wastewater enters the aeration tank at several points along the length of the tank. Step feed is typically applied during high flow events. In conventional treatment mode the activated sludge is transferred to the secondary clarifier during high flow rates. The transfer of solids often results in a significant increase in secondary effluent TSS.  Switching to step feed mode and adding the wastewater at several points along the aeration tank, results in a significant reduction in the transfer of activated sludge from the aeration basin to the secondary clarifier. Switching to step feed in a timely manner for the duration of the storm event results in only a minor increase in secondary effluent TSS.

The full benefits of step feed are best realized if the operations staff switch to step feed mode several hours before the high flow enters the treatment plant. By implementing step feed early the majority of the nitrifying bacteria are stored in the first pass of the aeration basin, while up to 90% of the storm flow is diverted to the last pass of the aeration basin. It takes approximately two hours following the change to step feed for the biomass to be stored in the first pass of the aeration basin. The average day flow rate for February 2019 was 1,086 m3/d. On February 5th the flow rate was 1,969 m3/d, and represented the first opportunity to demonstrate step feed. Unfortunately the high flow event occurred at night when no operations staff were on-site to manually open the step feed gates.

## Impact of not implementing step feed – case study

The impact on the distribution of activated sludge by staying in conventional treatment mode, is summarized in Table 4. Bancroft WWTP is required to nitrify, therefore it is always desirable the maximum quantity of activated sludge is under aeration where nitrification occurs. The case study covers a three day period in February 2019. On February 4th the flow rate was 1,458 m3/d. The mass of activated sludge under aeration was 3,694 kg (67%), and 933 kg (17%) in the secondary clarifier. On February 5th the flow rate was 1,969 m3/d. The mass of activated sludge under aeration was 1,983 kg (29%), and 4,321 kg (64%) in the secondary clarifier. Staying in conventional treatment mode during the high flow event resulted in the transfer of the activated sludge out of the aeration basin, and into the secondary clarifier. On February 6th the flow rate was 988 m3/d. The mass of activated sludge under aeration was 3,995 kg (70%), and 763 kg (14%) in the secondary clarifier. The flow rate on February 6th was similar to February 4th, and resulted in the re-distribution of activated sludge and a return to similar conditions as February 4th. During the three day period the mass and percentage of activated in the anoxic tank remained generally the same.

If the operations staff had been on-site and were able to implement step feed, the transfer of activated sludge from the aeration basin to the secondary clarifier on February 5th would not have occurred. The distribution of activated sludge would have been the same on February 5th as it was on February 4th and 6th.

Table 4. Activated Sludge Re-Distribution Caused by High Flow Rate.

# capacity demonstration

Technical assistance was implemented in February 2018. The objective was to demonstrate stable process control by implementing a higher and more stable level of process control. Experience from establishing stable process control at similarly sized WWTPs across Ontario since 1990 indicated there was latent capacity in the major unit processes at Bancroft WWTP. On June 1st 2018, liquid train 2 was placed on standby and all of the raw wastewater was treated in liquid train 1. Liquid train 1 successfully treated the wastewater flow and loading through March 2019. Liquid train 2 only was in service from March to September 2019. September 2019 marked the formal completion of the capacity demonstration. Between October 2019 and March 2020 the main activities included writing the CTA report and preparing the application to the MECP to re-rate the treatment plant to 2,000 m3/d.

## Waste Activated Sludge Thickening Study

Operations staff had not demonstrated achieving the 240 day MECP biosolids storage guideline. In July 2018, a study to increase the concentration of the Waste Activated Sludge (WAS) was implemented. The steps involved inserting an on/off cycle in the RAS pump control. The cycle control stopped the RAS pump for a selected period of time that enabled the RAS concentration to increase. By increasing the RAS concentration, the required WAS flow rate to maintain stable process control was significantly reduced. The results of the study are summarized in Table 5.

Table 5. Results of WAS Thickening Study

Demonstrating the 240 day storage time was a major milestone that enabled the operations staff to be confident the on-site biosolids storage was capable. Figure 33 is a graphical representation of the storage time using seven day moving average. The orange horizontal trace is the MECP 240 day storage guideline. In February 2019 the operations staff achieved the 240 day guideline for the first time, at a WAS flow rate of 6 m3/d.  The lowest WAS flow rate demonstrated was 5.4 m3/d equivalent to a storage time of 288 days.

Figure 33. Achieving the MECP Biosolids Storage Guideline

## results of the capacity demonstration

Discussions with MECP stakeholders indicate the re-rated flow rate demonstrated in liquid train 1 from July 2018 to September 2019 is 2,000 m3/d. Once approved, the increase equates to a 22 % increase in capacity that was funded by the capital upgrade completed in 2009.

# conclusions

## viability of existing major unit processes

The capacity demonstration revealed the existing major unit processes are capable at both current and future flow rates. Only liquid train 1 was in service from June 2018 to May 2019.  Only liquid train 2 was in service from May to September 2019. During these periods both trains operated successfully. The only period of higher treated effluent TAN was January through May 2019 coinciding with high flow rates and only one liquid train in service.

## Total sludge mass control program

The manager of the WWTP was already knowledgeable of the total sludge mass control concept prior to the start of the project, and had implemented the program in both liquid trains in December 2017. The treatment plant manager successfully maintained an adequate barrier of activated sludge to consistently nitrify, in both liquid trains throughout the project.

## raw wastewater characteristics

While the characteristics of the raw wastewater in the Town of Bancroft are considered residential in nature, January 2018 was an exception. Some of the individual sample results for raw wastewater concentrations for BOD, TSS, TP, and TKN were all higher than typical residential values. The results indicate there may be a presence of commercial wastewater discharging to the sewer. There was a re-occurrence of higher than typical raw wastewater values in 2019, however not to the same extent as 2018.

## stable process control

Operations staff are independently making the correct data based decisions to maintain stable process control. The secondary clarifiers continue to function well and are effectively returning the settled activated back to the anoxic tank and aeration basins. During dry weather the majority of the activated sludge is either in the anoxic tank or aeration basin. The low percentage of activated sludge in liquid train 2 secondary clarifier is explained by the newer and better designed sludge removal equipment.

## sludge accountability

The sludge accountability analysis completed for 2018 closed within 1.8 %. The difference between the projected sludge mass produced and the reported was less than 4 kg per day. This is an excellent level of accountability and means that the flow rates and current sampling program are representative and there is a high level of confidence about the accuracy of the reported TSS loading to the York River.

## step feed

The many benefits of step feed are best realized by switching to step feed mode several hours before the flow rate increases. February 5th 2019 presented the best opportunity to demonstrate step feed, however the high flow event occurred at night when no operations staff were on-site to manually open the step feed gates. To date, the application of step feed as an effective storm flow management tool has not been possible.

# RECOMMENDATIONS

## Maintaining the existing physical infrastructure and equipment

It is projected the rerated flow rate of 2,000 m3/d will be reached in 2040. This is a significant period of time the Town of Bancroft does not have to provide capital funds for upgrades. It is recommended that adequate resources are budgeted to ensure the existing physical infrastructure and associated equipment are maintained in operating condition.

## viability of existing major unit processes

It is recommended to rerate the existing major unit processes to 2,000 m3/d. When operating only one liquid train, it is recommended to keep the train not in service full with treated water and the mechanical equipment running. This will enable the operating staff to quickly switch from one train to another if there is a failure of equipment during the winter season.

## institutionalization of THE OPTIMIZATION PROGRAM

In 2009, the Town of Bancroft elected to implement a $9 million capital upgrade without first optimizing the existing human and physical infrastructure. If the facility had been optimized and the same 22% latent capacity was discovered prior to 2009, the Town of Bancroft may have decided  the capital investment was either not required, or could be deferred. It is recommended the MECP and FCM formally adopt a policy requiring municipalities to thoroughly investigate the capability of both the human and physical infrastructure prior to proceeding with expensive capital upgrades. Without such a policy, other municipalities in Ontario and across Canada are at risk of stressing their tax payers by pre-maturely electing to implement expensive capital upgrades, that are not actually required.

## raw wastewater characteristics

In January 2018, the individual sample results for raw wastewater concentrations for BOD, TSS, TP, and TKN were all higher than typical residential values. All four parameters being higher than typical would indicate the presence of some commercial influence. It is recommended to implement a sewer sampling program. The objective of the sampling program is to identify the source of the high BOD, TSS, TP, and TKN.

## stable process control

Operations staff continue to independently make the correct data based decisions to maintain stable process control. It is recommended to continue with the same high level of process control demonstrated during the capacity demonstration. Maintaining the high level of process control will also support maintaining the excellent level of sludge accountability reported for 2018.

## Step feed

It is recommended to automate the step feed gates and equipment in both liquid trains. This upgrade will provide the required flexibility for operations staff to maximize the performance of the re-rated treatment plant. It is anticipated that climate change will result in more frequent and more intense storm events. Having the ability to quickly switch from conventional treatment to step feed is the level of operational flexibility that operations staff require going forward.

## operational strategy

It is recommended to when possible, operate train 2 instead of train 1 to take advantage of the better design of the secondary clarifier sludge removal equipment.